## A1
#VALUE! |  |  |  |  | PIPING MATERIAL SPECIFICATION | [10 empty] | Rev: C0
[5 empty] | Piping Class |  |  |  | Material |  |  | C.A |  | Mill Tol |  | Sheet No.
[5 empty] | A1 |  | 150# |  | CS |  |  | 3 mm |  | 12.5% |  | 24
[5 empty] | Design Code: |  |  | ASME B 31.3
[5 empty] | Service: |  | Cooling Water, Diesel, Steam, WI, HC with low CO2 and H2S, Fresh Water, Hydraulic, Nitrogen, Exhaust, Fuel Oil, Tank Air Vent
[5 empty] | Branch Chart: |  |  | Ref. APPENDIX-1, Chart 1
Pressure-Temperature Rating
Press., barg | 19.6 |  | 19.2 |  | 17.7 |  | 15.8 |  | 13.8 | [5 empty] | Hydrotest Pr. (barg)
Temp., °C | -29 to 38 |  | 50 |  | 100 |  | 150 |  | 200 | [5 empty] | 29.4
Pipe Data
Code | ASME B 36.10M
Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24
O.D.mm | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4 | 457 | 508 | 559 | 610
Sch. | 160 | 160 | 160 | 160 | 80 | 80 | 80 | 80 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | - | 40
WT. mm | 7.47 | 5.56 | 6.35 | 7.14 | 5.54 | 7.62 | 8.56 | 10.97 | 8.18 | 9.27 | 10.31 | 11.1 | 12.7 | 14.27 | 15.1 | 15.88 | 17.47
TYPE | Seamless | [12 empty] | EFW, 100% RT
MOC | ASTM A 106 Gr. B | [12 empty] | ASTM A 671 - CC60 Class 22
Ends | BE
Fittings Data
TYPE | Butt Weld (SCH to match pipe), Seamless | [12 empty] | Butt Weld (SCH to match pipe), Welded
MOC | ASTM A 234 Gr. WPB | [12 empty] | ASTM A 420 Gr. WPL6
Elbow | ASME B 16.9
Tee | ASME B 16.9
Red. | ASME B 16.9
Cap | ASME B 16.9
Plug | Hex Head Plug, ASME B 16.11
Weldolet | MSS SP 97, ASTM A 105N
Flange
MOC | ASTM A 105N
FACE | 300# RF, Serrated Finish
TYPE | Weld Neck, ASME B 16.5, Butt Welding ends as per ASME B 16.25
Spectacle Blind/Spacer Blinds
MOC | ASTM A 105N
Spectacle | ASME B 16.48 | [10 empty] | Spacer and blind as per ASME B 16.48
Bolts/ Nuts/ Gaskets
Stud Bolts | ASTM A 193 Gr. B7M, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Hex Nuts | ASTM A 194 Gr. 2HM, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Gasket | ASME B 16.20, 4.5mm, SS316/SS316L Spiral Wound with Flexible Graphite (F.G.) filler
Valves
Rating | 150#, RF
Ball | BSRA1R, BSFA1R
Gate | GAWA1R
Globe | GLSA1R
Check | CHPA1R |  |  |  | CSWA1R, CDPA1R
Notes
1. PMS to be read in conjunction with Piping Design Basis, Doc No. 50502-SPE- 80000-PP-BD-0001 and Valve Material Specification, Doc. No. 50502-SPE- 80000-PP-SP-0002.
2. Weld Joint Factor for welded pipe shall be as per ASME B 31.3.
3. Welded fittings shall be 100% radiographed.
4. Two jackscrew, 180 degree apart shall be provided in one of the flanges for all orifice flange and specified spectacle blind assemblies.
5. Spectacle blinds and spacer sizes and rating that are not available in ASME B 16.48 shall be as per manuf. standard. Design shall be submitted to Company for review and approval.
6. Maximum temperature limit for all Soft Seat Ball Valve shall be 200°C.
7. Wafer check valve to be avoided, unless the available space constraint does not allow normal check valve.

## B1
#VALUE! |  |  |  |  | PIPING MATERIAL SPECIFICATION | [10 empty] | Rev: C0
[5 empty] | Piping Class |  |  |  | Material |  |  | C.A |  | Mill Tol |  | Sheet No.
[5 empty] | B1 |  | 300# |  | CS |  |  | 3 mm |  | 12.5% |  | 25
[5 empty] | Design Code: |  |  | ASME B 31.3
[5 empty] | Service: |  | Cooling Water, Diesel, WI, HC with low CO2 and H2S, Steam, Hydraulic
[5 empty] | Branch Chart: |  |  | Ref. APPENDIX-1, Chart 1
Pressure-Temperature Rating
Press., barg | 51.1 |  | 50.1 |  | 46.6 |  | 45.1 |  | 43.8 | [5 empty] | Hydrotest Pr. (barg)
Temp., °C | -29 to 38 |  | 50 |  | 100 |  | 150 |  | 200 | [5 empty] | 76.65
Pipe Data
Code | ASME B 36.10M
Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24
O.D.mm | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4 | 457 | 508 | 559 | 610
Sch. | 160 | 160 | 160 | 160 | 80 | 80 | 80 | 80 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | - | 40
WT. mm | 7.47 | 5.56 | 6.35 | 7.14 | 5.54 | 7.62 | 8.56 | 10.97 | 8.18 | 9.27 | 10.31 | 11.1 | 12.7 | 14.27 | 15.1 | 15.88 | 17.47
TYPE | Seamless | [12 empty] | EFW, 100% RT
MOC | ASTM A 106 Gr. B | [12 empty] | ASTM A 671 - CC60 Class 22
Ends | BE
Fittings Data
TYPE | Butt Weld (SCH to match pipe), Seamless | [12 empty] | Butt Weld (SCH to match pipe), Welded
MOC | ASTM A 234 Gr. WPB | [12 empty] | ASTM A 420 Gr. WPL6
Elbow | ASME B 16.9
Tee | ASME B 16.9
Red. | ASME B 16.9
Cap | ASME B 16.9
Plug | Hex Head Plug, ASME B 16.11
Weldolet | MSS SP 97, ASTM A 105N
Flange
MOC | ASTM A 105N
FACE | 300# RF, Serrated Finish
TYPE | Weld Neck, ASME B 16.5, Butt Welding ends as per ASME B 16.25
Spectacle Blind/Spacer Blinds
MOC | ASTM A 105N
Spectacle | ASME B 16.48 | [10 empty] | Spacer and blind as per ASME B 16.48
Bolts/ Nuts/ Gaskets
Stud Bolts | ASTM A 193 Gr. B7M, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Hex Nuts | ASTM A 194 Gr. 2HM, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Gasket | ASME B 16.20, 4.5mm, SS316/SS316L Spiral Wound with Flexible Graphite (F.G.) filler
Valves
Rating | 300#, RF
Ball | BSRB1R, BSFB1R
Gate | GAWB1R
Globe | GLSB1R
Check | CHPB1R |  |  |  | CSWB1R, CDPB1R
Notes
1. PMS to be read in conjunction with Piping Design Basis, Doc No. 50502-SPE- 80000-PP-BD-0001 and Valve Material Specification, Doc. No. 50502-SPE- 80000-PP-SP-0002.
2. Weld Joint Factor for welded pipe shall be as per ASME B 31.3.
3. Welded fittings shall be 100% radiographed.
4. Two jackscrew, 180 degree apart shall be provided in one of the flanges for all orifice flange and specified spectacle blind assemblies.
5. Spectacle blinds and spacer sizes and rating that are not available in ASME B 16.48 shall be as per manuf. standard. Design shall be submitted to Company for review and approval.
6. Maximum temperature limit for all Soft Seat Ball Valve shall be 200°C.
7. Wafer check valve to be avoided, unless the available space constraint does not allow normal check valve.

## D1
#VALUE! |  |  |  |  | PIPING MATERIAL SPECIFICATION | [10 empty] | Rev: C0
[5 empty] | Piping Class |  |  |  | Material |  |  | C.A |  | Mill Tol |  | Sheet NO
[5 empty] | D1 |  | 600# |  | CS |  |  | 3 mm |  | 12.5% |  | 26
[5 empty] | Design Code: |  |  | ASME B 31.3
[5 empty] | Service: |  | Cooling Water, Diesel, WI, HC with low CO2 and H2S, Steam, Hydraulic
[5 empty] | Branch Chart: |  |  | Ref. APPENDIX-1, Chart 1
Pressure-Temperature Rating
Press., barg | 102.1 |  | 100.2 |  | 93.2 |  | 90.2 |  | 87.6 | [5 empty] | Hydrotest Pr. (barg)
Temp., °C | -29 to 38 |  | 50 |  | 100 |  | 150 |  | 200 | [5 empty] | 153.15
Pipe Data
Code | ASME B 36.10M
Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24
O.D.mm | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4 | 457 | 508 | 559 | 610
Sch. | 160 | 160 | 160 | 160 | 160 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
WT. mm | 7.47 | 5.56 | 6.35 | 7.14 | 8.74 | 7.62 | 8.56 | 10.97 | 12.7 | 15.08 | 17.47 | 19.05 | 21.44 | 23.82 | 26.19 | 28.57 | 30.96
TYPE | Seamless | [12 empty] | EFW, 100% RT
MOC | ASTM A 106 Gr. B | [9 empty] | ASTM A 333 Gr.6 |  |  | ASTM A 671 - CC60 Class 22
Ends | BE
Fittings Data
TYPE | Butt Weld (SCH to match pipe), Seamless | [12 empty] | Butt Weld (SCH to match pipe), Welded
MOC | ASTM A 234 Gr. WPB | [9 empty] | ASTM A 420 Gr. WPL6
Elbow | ASME B 16.9
Tee | ASME B 16.9
Red. | ASME B 16.9
Cap | ASME B 16.9
Plug | Hex Head Plug, ASME B 16.11
Weldolet | MSS SP 97, ASTM A 105N
Flange
MOC | ASTM A 105N
FACE | 600# RF, Serrated Finish
TYPE | Weld Neck, ASME B 16.5, Butt Welding ends as per ASME B 16.25
Spectacle Blind/Spacer Blinds
MOC | ASTM A 105N
Spectacle | ASME B 16.48 | [10 empty] | Spacer and blind as per ASME B 16.48
Bolts/ Nuts/ Gaskets
Stud Bolts | ASTM A 193 Gr. B7M, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Hex Nuts | ASTM A 194 Gr. 2HM, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Gasket | ASME B 16.20, 4.5mm, SS316/SS316L Spiral Wound with Flexible Graphite (F.G.) filler
Valves
Rating | 600#, RF
Ball | BSRD1R, BSFD1R
Gate | GAWD1R
Globe | GLSD1R
Check | CHPD1R |  |  |  | CSWD1R, CDPD1R

## E1
#VALUE! |  |  |  |  | PIPING MATERIAL SPECIFICATION | [10 empty] | Rev: C0
[5 empty] | Piping Class |  |  |  | Material |  |  | C.A |  | Mill Tol |  | Sheet No.
[5 empty] | E1 |  | 900# |  | CS |  |  | 3 mm |  | 12.5% |  | 27
[5 empty] | Design Code: |  |  | ASME B 31.3
[5 empty] | Service: |  | Diesel, WI, HC with low CO2 and H2S, Steam, Hydraulic
[5 empty] | Branch Chart: |  |  | Ref. APPENDIX-1, Chart 1
Pressure-Temperature Rating
Press., barg | 153.2 |  | 150.4 |  | 139.8 |  | 135.2 |  | 131.4 | [5 empty] | Hydrotest Pr. (barg)
Temp., °C | -29 to 38 |  | 50 |  | 100 |  | 150 |  | 200 | [5 empty] | 229.8
Pipe Data
Code | ASME B 36.10M
Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24
O.D.mm | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114 | 168.3 | 219 | 273.1 | 323.9 | 355.6 | 406.4 | 457 | 508 | 559 | 610
Sch. | 160 | 160 | 160 | 160 | 160 | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
WT. mm | 7.47 | 5.56 | 6.35 | 7.14 | 8.7 | 11.12 | 11.1 | 14.27 | 18.3 | 21.44 | 25.4 | 27.79 | 30.96 | 34.92 | 38.1 | 41.27 | 46.02
TYPE | Seamless | [12 empty] | EFW, 100% RT
MOC | ASTM A 106 Gr. B | [7 empty] | ASTM A 333 Gr.6 |  |  |  |  | ASTM A 671 - CC60 Class 22
Ends | BE
Fittings Data
TYPE | Butt Weld (SCH to match pipe), Seamless | [12 empty] | Butt Weld (SCH to match pipe), Welded
MOC | ASTM A 234 Gr. WPB | [7 empty] | ASTM A 420 Gr. WPL6
Elbow | ASME B 16.9
Tee | ASME B 16.9
Red. | ASME B 16.9
Cap | ASME B 16.9
Plug | Hex Head Plug, ASME B 16.11
Weldolet | MSS SP 97, ASTM A 105N
Flange
MOC | ASTM A 105N
FACE | 1500#, RTJ |  |  |  | 900#, RTJ
TYPE | Weld Neck, ASME B16.5, Butt welding ends as per ASME 16.25, Note 8,9
Spectacle Blind/Spacer Blinds
MOC | ASTM A 105N
Spectacle | ASME B 16.48 | [10 empty] | Spacer and blind as per ASME B 16.48
Bolts/ Nuts/ Gaskets
Stud Bolts | ASTM A 193 Gr. B7M, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Hex Nuts | ASTM A 194 Gr. 2HM, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Gasket | ASME B 16.20, OCT ring of Soft Iron with Max. Hardness of 90 BHN, HDG
Valves
Rating | 900#, RTJ
Ball | USE GATE VALVE |  |  |  | BSRE1J, BSFE1J
Gate | GAWE1J
Globe | GLSE1J
Check | CHPE1J |  |  |  | CSWE1J, CDPE1J
DBB (Inst) | DSRE1JT
DBB | DSRE1J, DSFE1J
Notes
1. PMS to be read in conjunction with Piping Design Basis, Doc No. 50502-SPE- 80000-PP-BD-0001 and Valve Material Specification, Doc. No. 50502-SPE- 80000-PP-SP-0002.
2. Weld Joint Factor for welded pipe shall be as per ASME B 31.3.
3. Welded fittings shall be 100% radiographed.
4. Two jackscrew, 180 degree apart shall be provided in one of the flanges for all orifice flange and specified spectacle blind assemblies.
5. Spectacle blinds and spacer sizes and rating that are not available in ASME B 16.48 shall be as per manuf. standard. Design shall be submitted to Company for review and approval.
6. Maximum temperature limit for all Soft Seat Ball Valve shall be 200°C.
7. Wafer check valve to be avoided, unless the available space constraint does not allow normal check valve.
8. Gasket Contact Surface shall have maximum roughness of 63AARH.
9. Minimum RTJ groove hardness shall be 120 BHN.